# Mechanical Specifications

WHISPERTHERM™ WATER SOURCE AIR CONDITIONER WITH THERMAL RECOVERY UNIT (TRU) AND HYDRONIC HEAT

PART 1 GENERAL

  - SECTION INCLUDES

# A. Vertical Stack Water Source Air Conditioner with Hydronic Heat

  - RELATED SECTIONS

  - REFERENCES

- ETL Listed under Underwriters Laboratories Standard for Safety UL1995 for heat pumps.

- AHRI ISO Standard 13256-1

  - DELIVERY, STORAGE AND HANDLING

- Deliver products to site, store and protect from the weather and construction debris.  Air conditioner cabinets and refrigeration chassis must be individually packaged and be tagged with site location, model number and configuration.

  - ENVIROMENTAL REQUIREMENTS

- Protect units from construction debris by covering all openings prior to start-up of the equipment.  Units must not be used for heating, cooling, or ventilation prior to the start-up of equipment for permanent use.  Use of the equipment for the temporary heating, cooling or ventilation is prohibited.

  - FACTORY TESTING

## All units shall be factory tested at normal operating conditions.  Cabinets and fans shall be tested to verify proper fan and control operation.  Refrigeration chassis shall be factory tested with cataloged water flow rates and sequenced to verify the proper operation of safety controls.  Testing without utilizing cataloged water flow rates is unacceptable.  All factory risers shall be pressure tested for leaks.

  - SUBMITTAL DOCUMENTATION

- Standard submittals shall include capacities, drawings, electrical data, installation, operation and maintenance manuals and other details.

PART 2 PRODUCTS

  - TYPE

- Vertical Stack Water Source Air Conditioner with integral risers, hot water heating coil, discharge arrangements, hose kits, and all accessories (ADD SPECIFIC OPTIONS HERE).  Units shall be standard operating range 75°F to 120°F (23.9°C to 48.9°C) entering fluid temperature for water source air conditioning applications.

  - CAPACITY

- Shall be as indicated on the drawings, which are based on Whalen units.  Capacities shall be certified under AHRI ISO Standard 13256-1.

  - CABINETS

- The one-piece unit cabinet shall be fabricated of reinforced 22-gauge continuous G60 galvanized steel.  All internal assemblies shall be welded and treated to prevent corrosion.

- The cabinet shall be insulated with 1/2-inch thick 2-pound density thermal and acoustical fiberglass insulation meeting material standard ASTM-C1071 and have an integral water repellent.  The insulation shall have a fungi and bacteria resistant barrier with no growth conforming to ASTM-C1338, ASTM G21 and ASTM G22 and meet fire safety standards under NFPA90A and NFPA90B. (OPTION) 1-inch thick 1-1/2-pound density thermal and acoustical fiberglass insulated discharge plenum.

- The cabinet shall allow the placement of vertical risers on any side not being used for service access or discharge air openings.

- The cabinet will have slots with edge protectors to accommodate movement of the risers with the isolation valves affixed (see 2.05 B).  The slots shall remain covered with insulation to minimize air infiltration.

- Cabinet return and discharge air openings shall be factory cut and flanged on all sides.  All insulation located behind cabinet openings must be removed by the unit manufacturer prior to shipment.  Knockouts for field cutting are unacceptable.

- Cabinet design shall allow a minimum 5-inches below the chassis access opening to allow for full height baseboard.

- (OPTION) A factory installed vibration isolation pad shall be installed on the bottom of the unit.

- The air conditioner cabinets shall be shipped separately from, and prior to the refrigeration chassis for early installation at the jobsite.

- Cabinet design shall allow removal of the refrigeration chassis without a requirement to first remove the main fan or thermal recovery unit.

- Cabinet design shall allow removal of the thermal recovery unit without a requirement to first remove the chassis or main fan.

- Cabinet design shall include means to connect and seal the supply air opening to the Acoustical Air Panel mounted per Whalen instructions.

- Cabinet design shall offer ventilation air connections on its top. (OPTION 1) Alternate ventilation air connections available, on rear and/or one side, for air to and from the outdoors.

- Cabinet design shall include internal channels to direct air from the exhaust air inlet connection, through the thermal recovery core, and to the exhaust air exit connection.

- Cabinet design shall include internal channels to direct air from the outdoor air inlet connection, through the thermal recovery core, and to the supply side of the chassis air coil.

  - REFRIGERATION CHASSIS

- The refrigeration chassis consisting of the compressor, air coil, water coil, expansion device, receiver, filter-drier, hot water heating air coil and safety controls shall be slide-rail base mounted in the cabinet, and shall be designed for easy removal after disconnecting the two hoses and a polarized electrical power plug.

- The compressor shall be the sealed hermetic type approved and tested for reverse cycle operation.  Internal thermal overload protection shall be provided.  The compressor shall be internally isolated and externally hard rubber mounted to the floating chassis.  Compressor motors shall be permanent split capacitor (PSC) type.  The compressor shall not operate on a call for heating.

- The air coils shall be copper tubes mechanically bonded to aluminum fins, multi-circuited to insure maximum coil distribution and effectiveness, and a minimum of three rows deep.  The coil shall be rated to withstand 600 psig refrigerant working pressure.  Face velocity shall not exceed 400 feet per minute to insure quiet operation and positive condensate drainage.

- The water coils shall incorporate an electro-coated steel outer tube and a copper inner tube.  The inner tube shall be spirally fluted and bonded to the outer tube to insure controlled refrigerant velocity and distribution. The coil shall be rated to withstand 650 psig refrigerant and 400 psig fluid working pressures.  (OPTION) Provide Cupro-nickel COAX coil.

- The hot water heating air coil shall be copper tubes mechanically bonded to the aluminum fins, multi-circuited to insure maximum coil distribution and effectiveness and a minimum of two (OPTION: three) rows deep.  Face velocity shall not exceed 400 feet per second to insure quiet operation.  The refrigeration circuit shall not operate on a call for heating.

- A three-way, two-position (On/Off) electric control valve (30 psi differential pressure) shall be factory mounted and wired into the refrigeration chassis to divert fluid flow between the water to refrigerant coil and hot water heating air coil.  (OPTION) Provide two, two-way, two-position (On/Off) electric control valves (30 psi differential pressure) in lieu of a three-way control valve for variable flow systems.  The valves shall factory mounted and wired into the refrigeration chassis to prevent fluid flow to the unit when a call for cooling or heating is not present.

- (OPTION) Automatic flow control valve – An automatic flow control valve shall be provided with each chassis and be factory preset for a fixed flow rate regardless of system pressure.  Each automatic balancing valve shall be capable of operation over a pressure differential range of 2 to 80 PSID.  Valves must utilize threaded connections and be easily removable for cleaning and maintenance.

- The chassis shall be shipped separately from the WSHP cabinets to prevent exposure to, and fouling from finishing work.

  - RISERS

- The unit manufacturer shall furnish Type M (OPTION: Type L) copper supply and return condenser water risers as an integral factory-assembled component of the heat pump.  Supply and return risers shall be protected by a galvanized steel pipe chase the length of the cabinet.  (OPTION) Provide (3/8) (1/2)-inch thick closed-cell riser insulation the length of the cabinet for ground-source applications.

- Ball-type isolation valves shall be factory assembled on the risers by the heat pump manufacturer.  The chassis shall be connected to the isolation valves through high-pressure stainless steel hoses provided by the unit manufacturer, to isolate compressor noise and vibration from the piping system.  Connection of the refrigerant chassis to building water system through the use of unions is unacceptable.

- The unit manufacturer shall furnish the air conditioner cabinet with the supply and return risers connected together (short circuited) between the isolation valves to facilitate flushing by bypassing water directly into the return loop without the water passing thru any device in the unit (i.e. refrigeration chassis, automatic flow control valve).

- The condensate drain riser shall be Type M copper and insulated the length of the cabinet with 3/8-inch closed-cell insulation.

  - DRAIN PAN

- The drain pan shall collect and drain condensate that may form from any component internal to the heat pump and shall be fabricated of welded and soldered 20 Ga. 304 stainless steel.  The copper condensate drain shall be rolled and soldered into the pan.

  - FANS

- The fan shall be slow speed forward curved centrifugal type capable of two fan speeds, and shall be accessible for removal and maintenance through the return air opening.

  - MOTORS

- Fan motors for heat pumps under 2-ton shall be of the permanently lubricated PSC standard or hi-static pressure (OPTION: ECM) type, as required; suitable for the current characteristics shown on the drawings, and shall have built-in thermal overload protection.

- Fan motors for heat pumps 2-ton and above shall be of the permanently lubricated constant-torque ECM (OPTION: constant-volume ECM) type, suitable for the current characteristics shown on the drawings, and shall have built-in overload protection.

- Motors shall be plug-in, multi-speed type with 1050-RPM maximum.

- (OPTION) Provide a two-speed fan switch located behind the acoustic return air panel.  The fan switch must be configurable for use with available fan speed motor taps.

  - SUPPLY GRILLES

- (STANDARD) The supply grilles shall be of the single deflection type fabricated of clear anodized aluminum.  All supply openings shall be painted black with a damper assembly and sight baffle provided when one unit is serving two separate rooms.

(OPTION 1) The supply grilles shall be of the single deflection type fabricated of (factory white painted extruded aluminum) or (custom painted extruded aluminum) (SELECT ONE).  All supply openings shall be painted black with a damper assembly and sight baffle provided when one unit is serving two separate rooms.

(OPTION 2) The supply grilles shall be of the double deflection type fabricated of (clear anodized extruded aluminum), (factory white painted extruded aluminum) or (custom painted extruded aluminum) (SELECT ONE).  All supply openings shall be painted black with a damper assembly and sight baffle provided when one unit is serving two separate rooms.

  - RETURN AIR PANEL

- (STANDARD) Unit Mounted Acoustical Panel - The return air opening shall be covered with a standard solid hinged front acoustical panel with return air entering through the bottom, top and both sides.  The front panel shall be fabricated of etched galvanized steel painted appliance white.  The return air panel shall allow for filter maintenance without the use of tools and be secured shut via magnets.  The door opening shall be sized to allow direct removal of the cabinet inner panel and refrigeration chassis.

- The supply air section of the panel shall include a removable hinged door secured shut by magnets. The door opening shall be sized to allow either servicing or direct removal of the thermal recovery unit. The door shall house the supply air grille, sized per schedule.

- Standard supply air grille opening shall include snap-in style spring clip on each side to secure the supply air grille.  Grilles shall be shipped with return air panel but NOT INSTALLED in the removable hinged door.

  - FILTERS

## (STANDARD) Filters shall be 1” thick disposable fiberglass media, MERV 4.

(OPTION 1) Filters shall be 1” thick disposable pleated media, MERV 8.

(OPTION 2) Filters shall be 1” thick disposable pleated media, MERV 13.

(OPTION 3) Filters shall be 1” thick permanent aluminum cleanable media, MERV 4.

  - THERMAL ENERGY RECOVERY SECTION / OUTDOOR AIR

- Cabinets shall be supplied with a thermal recovery unit that is easily accessible and removable for servicing. Duct connections for the thermal recovery unit shall be standard 5 inch diameter.

- The thermal recovery unit shall be fabricated from heavy-gauge galvanized steel. A ½ inch drain hose emptying into the cabinet drain pan shall be provided. A positive closing damper shall be included on the exhaust air discharge duct connection. Electrical connection for the module shall be made by a male plug into a female receptacle supplied in the cabinet.

- Air filters shall be supplied for the fresh air and exhaust air flows. Filters shall be easily serviced or replaced through the front of the unit. Filters shall be washable.

- The thermal recovery unit shall house fresh air and exhaust air blowers. Blowers shall be statically and dynamically balanced, direct drive, single phase with integral thermal overload protection. The blower wheel shall be the forward-curved SWSI centrifugal type.

- The fresh air and exhaust air blower speed shall be set at the factory.

- The thermal recovery core shall be protected by a defrost sensor that terminates operation of the fresh air blower.

- (OPTION 2) An optional timed washroom exhaust control with reset to be provided with decorative momentary switch to activate the exhaust fan for a maximum of 20 minutes.

- (OPTION 3) Factory set dedicated constant ventilation rate selection 1) 25 CFM 2) 35 CFM 3) 50 CFM 4) 70 CFM 5) 90 CFM.

- (OPTION 4) Factory set nominal intermittent exhaust rate high speed selection 1) 100 CFM 2) 150 CFM when used in conjunction with optional timed momentary switch.

  - POWER SUPPLY

- Single point field power connection is made to unit junction box through either of the 7/8" knockouts located on the side or on the top of the cabinet as shown on the drawings.

(OPTION 1) Each unit shall include a non-fused disconnect switch, factory mounted and wired.

(OPTION 2) Each unit shall include a fused disconnect switch, factory mounted and wired.

  - CONTROLS

- Unit shall include a solid-state control board as part of the unit control system incorporating these features:

  - Random start compressor protection.

  - Anti-short cycle compressor minimum OFF time delay.

  - Safety controls that protect the compressor from the following conditions:

    - High pressure

    - Low airflow

    - Low liquid flow

    - Low entering air temperature

    - Brown-out power conditions

    - Condensate Overflow Protection

  - Status LED indicating the device causing a fault condition.

  - Soft lockout feature that provides for an automatic reset prior to the initiation of a hard lockout.

  - Test mode capability with shortened time delays for servicing.

  - (OPTION 1) Low pressure

  - (OPTION 2) Low/High liquid temperature protection with three different settings based on liquid properties.

- The unit shall default to continuous ultra-low main fan speed if no call for Heating or Cooling.

- The thermal recovery unit shall have independent dedicated electrical power and both blowers shall operate continuously.

- (OPTION 1) Factory set dedicated constant ventilation rate selection 1) 25 CFM 2) 35 CFM 3) 50 CFM 4) 70

CFM 5) 90 CFM.

- (OPTION 2) Timed washroom exhaust control with reset to activate 100 CFM intermittent exhaust high fan speed for a maximum of 20 minutes. Factory set dedicated constant ventilation rate selection 1) 25 CFM 2) 35 CFM 3) 50 CFM 4) 70 CFM. (Decorative switches must be purchased separately. Multiple switches may be used for a single unit.)

- (OPTION 3) Timed washroom exhaust control with reset to activate 150 CFM intermittent exhaust high fan speed for a maximum of 20 minutes. Factory set dedicated constant ventilation rate selection 1) 35 CFM 2) 50 CFM 3) 70 CFM 4) 90 CFM. (Decorative switches must be purchased separately. Multiple switches may be used for a single unit.)

  - THERMOSTAT

- The heat pump manufacturer shall provide a 24-volt manual changeover wall thermostat with a HEAT-OFF-COOL system switch and AUTO-ON fan selector switch.

- On units up to two tons of cooling, the thermostat shall be unit mounted at a height of 48 inches from the bottom of the cabinet.  On units greater than two tons of cooling, the thermostat shall be remote mounted.

- Others shall install thermostat by plugging into the control wiring with a polarized male-female plug after the walls are finished when unit mounted or attaching to color coded pigtails when remote mounted.  High voltage, return air thermostats with remote bulbs subject to damage during routine service will not be accepted.

  - SPARE PARTS

- The installing contractor shall provide to the Owner one spare chassis for each fifty heat pumps of a given size.  (Add any additional spare parts requirements here).

## PART 3	EXECUTION

  - INSTALLATION

- Furnish as shown on the drawings and as specified herein, vertical stack water source heat pumps with integral risers, and with capacity and electrical characteristics as scheduled.  Units shall be Series VI as manufactured by The Whalen Company of Easton, MD.

- Install in accordance with manufacturer's installation instructions.  Install units plumb and level, and maintain manufacturer's recommended clearances for the unit and accessories.

- Follow manufacturer's recommendations for cleaning and flushing.