## Slide 1
Refrigerant Transition

## Slide 2: Refrigeration Transition Timeline

## Slide 3: Refrigeration Transition Timeline
Next Deadline
IMPORTANT

## Slide 4: AC / Heat Pump Transition Timeline
PRODUCT (sealed system)
SYSTEM
SYSTEM
Commercial & Residential Packaged (AC/HP)
VRF / VRV (AC/HP)

## Slide 5: Refrigerant Global Warming Potential
Whalen is using R-454B refrigerant
Lowest widely used GWP option to replace R-410A
  76% decrease vs R-410A
  34% decrease vs R-32
Ozone depletion of ZERO
Similar operation and efficiency to current R-410A products

## Slide 6: R-454B – A2L CLASS REFRIGERANT
R-454B is classified by ASHRAE as an A2L lower flammability refrigerant
UL 60335 2-40 safety standard requires products with more than 62 ounces of A2L refrigerant to contain a factory installed Refrigerant Detection
If a refrigerant leak is detected, the RDS triggers a system fault & the unit enters a mitigation mode to reduce leaked refrigerant concentration level

## Slide 7: Minimum Installation Area
Minimum area where a blower-equipped unit must be installed, and mechanical/natural ventilation is not required

## Slide 8
Questions?
Notes: 8