## Whisperline 1-stage
Job Details
Product line: Whalen Water to air WSHP/GSHP and AC
Selection Summary - General Info
Tag | VI-1 | VI-2 | VI-3 | VI-4 | VI-5 | VI-6 | VI-7 | VI-8 | VI-9
Model | VP-A-0204-B*C | VP-A-0304-B*C | VP-A-0404-B*C | VP-A-0504-B*B | VP-A-0604-B*B | VP-A-0804-B*B | VP-A-0814-B*D | VP-A-1004-B*D | VP-A-1204-B*D
Fan type | ECM - Constant torque | ECM - Constant torque | ECM - Constant torque | ECM - Constant torque | ECM - Constant torque | ECM - Constant torque | ECM - Constant torque | ECM - Constant torque | ECM - Constant torque
Fan speed | High | High | High | High | High | High | High | High | High
Fan motor speed | High | High | High | High | High | High | High | High | High
Ext. static pressure (in of water) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Fluid pressure drop (ft of water) | 4 | 9 | 7.9 | 10.1 | 12.9 | 18.9 | 16.4 | 16.7 | 18.7
Filter | MERV 4 | MERV 4 | MERV 4 | MERV 4 | MERV 4 | MERV 4 | MERV 4 | MERV 4 | MERV 4
Air grille | Flush mount chassis accessible | Flush mount chassis accessible | Flush mount chassis accessible | Flush mount chassis accessible | Flush mount chassis accessible | Flush mount chassis accessible | Flush mount chassis accessible | Flush mount chassis accessible | Flush mount chassis accessible
Has control valve | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Control valve (cV) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Selection Summary - Cooling
Tag | VI-1 | VI-2 | VI-3 | VI-4 | VI-5 | VI-6 | VI-7 | VI-8 | VI-9
Model | VP-A-0204-B*C | VP-A-0304-B*C | VP-A-0404-B*C | VP-A-0504-B*B | VP-A-0604-B*B | VP-A-0804-B*B | VP-A-0814-B*D | VP-A-1004-B*D | VP-A-1204-B*D
Entering dry bulb (°F) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
Entering wet bulb (°F) | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67
Leaving dry bulb (°F) | 63.7 | 61 | 60.9 | 59.9 | 60.5 | 60.9 | 58.9 | 60 | 59.4
Leaving wet bulb (°F) | 60.1 | 58.2 | 57.7 | 57.8 | 58.1 | 58.9 | 58.2 | 58.3 | 57.6
Air flow (CFM) | 307 | 347 | 435 | 543 | 678 | 897 | 868 | 1170 | 1313
Fluid type | Water | Water | Water | Water | Water | Water | Water | Water | Water
Ent. fluid temp. (°F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Leav. fluid temp. (°F) | 96 | 94.3 | 94.3 | 94.7 | 95.2 | 94.6 | 94.5 | 95 | 95.2
Fluid flow rate (GPM) | 1.5 | 2.5 | 3.3 | 3.9 | 4.5 | 6 | 6 | 7.5 | 9
Total capacity (btu/h) | 6725 | 9513 | 12615 | 15561 | 18909 | 23042 | 23790 | 31956 | 38668
Sensible capacity (btu/h) | 5362 | 7083 | 8876 | 11717 | 14179 | 18387 | 19620 | 25112 | 28991
Power input (W) | 442 | 617 | 816 | 957 | 1194 | 1683 | 1393 | 1641 | 2157
Energy efficiency ratio | 15.2 | 15.4 | 15.5 | 16.3 | 15.8 | 13.7 | 17.1 | 19.5 | 17.9
Total heat of rejection (Btu/h) | 8349 | 11753 | 15534 | 18848 | 23029 | 28790 | 28539 | 37570 | 46381
Selection Summary - Heating
Tag | VI-1 | VI-2 | VI-3 | VI-4 | VI-5 | VI-6 | VI-7 | VI-8 | VI-9
Model | VP-A-0204-B*C | VP-A-0304-B*C | VP-A-0404-B*C | VP-A-0504-B*B | VP-A-0604-B*B | VP-A-0804-B*B | VP-A-0814-B*D | VP-A-1004-B*D | VP-A-1204-B*D
Air flow (CFM) | 307 | 358 | 448 | 554 | 719 | 897 | 875 | 1170 | 1330
Entering dry bulb (°F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Leaving dry bulb (°F) | 94.7 | 102.7 | 100.6 | 100.3 | 98.5 | 100.9 | 100 | 98.4 | 99.3
Fluid type | Water | Water | Water | Water | Water | Water | Water | Water | Water
Ent. fluid temp. (°F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Leav. fluid temp. (°F) | 60.9 | 61.6 | 62.7 | 62.4 | 62 | 62.2 | 62.1 | 61.9 | 62.1
Fluid flow rate (GPM) | 1.5 | 2.5 | 3.3 | 3.9 | 4.5 | 6 | 6 | 7.5 | 9
Total heating capacity (btu/h) | 8249 | 12745 | 14908 | 18244 | 22276 | 30164 | 28552 | 36060 | 42344
Power input (W) | 411 | 656 | 825 | 1004 | 1226 | 1951 | 1452 | 1643 | 1981
Total heat of absorption (Btu/h) | 6732 | 10382 | 11964 | 14825 | 17946 | 23520 | 23610 | 30426 | 35584
Coefficient of performance | 5.88 | 5.69 | 5.29 | 5.32 | 5.32 | 4.53 | 5.76 | 6.43 | 6.26
Selection Summary - Electric
Tag | VI-1 | VI-2 | VI-3 | VI-4 | VI-5 | VI-6 | VI-7 | VI-8 | VI-9
Model | VP-A-0204-B*C | VP-A-0304-B*C | VP-A-0404-B*C | VP-A-0504-B*B | VP-A-0604-B*B | VP-A-0804-B*B | VP-A-0814-B*D | VP-A-1004-B*D | VP-A-1204-B*D
Voltage | 208-230 | 208-230 | 208-230 | 208-230 | 208-230 | 208-230 | 208-230 | 208-230 | 208-230
Min. circuit ampacity | 5.3 | 8.6 | 10.2 | 8.2 | 11.8 | 17.5 | 16.1 | 20 | 21.6
Max. overcurrent protection (amps) | 15 | 15 | 15 | 15 | 15 | 25 | 25 | 30 | 30
Selection Summary - Misc
Tag | VI-1 | VI-2 | VI-3 | VI-4 | VI-5 | VI-6 | VI-7 | VI-8 | VI-9
Model | VP-A-0204-B*C | VP-A-0304-B*C | VP-A-0404-B*C | VP-A-0504-B*B | VP-A-0604-B*B | VP-A-0804-B*B | VP-A-0814-B*D | VP-A-1004-B*D | VP-A-1204-B*D
Application notes | -- | -- | -- | -- | -- | -- | -- | -- | --
Notes | -- | -- | -- | -- | -- | -- | -- | -- | --
Unit type | Vertical Stack | Vertical Stack | Vertical Stack | Vertical Stack | Vertical Stack | Vertical Stack | Vertical Stack | Vertical Stack | Vertical Stack
Product series | Whisperline(R) | Whisperline(R) | Whisperline(R) | Whisperline(R) | Whisperline(R) | Whisperline(R) | Whisperline(R) | Whisperline(R) | Whisperline(R)
Configuration | Classic | Classic | Classic | Classic | Classic | Classic | Classic | Classic | Classic
Application | Standard heat pump | Standard heat pump | Standard heat pump | Standard heat pump | Standard heat pump | Standard heat pump | Standard heat pump | Standard heat pump | Standard heat pump
Notes:
Whalen is the Basis of Design and the standard for comparison. ClimateMaster, Bosch and Water Furnace are acceptable subject to compliance with schedule and notes.
All units shall be factory tested at cataloged operating conditions. Testing without utilizing cataloged water flow rates is unacceptable.
The unit cabinet shall be fabricated of 18 Gauge G90 galvanized steel with 1/2-inch closed cell thermal and acoustical elastomeric insulation.
Vertical units shall be internally trapped from the factory. Manufacturers who do not provide internal traps shall be responsible for additional Owner costs to field trap all units.
All units shall utilize sound attenuating compressor blankets to combine with sound attenuating material applied within the air handling compartment to further reduce sound transmitted while in operation.
The compressor shall be the sealed hermetic type with thermal overload protection and dual level floating vibration isolation system to minimize compressor vibration.
Compressor shall be located in an insulated compartment away from air stream to minimize sound transmission.
Drain pans shall be welded and soldered 20 Ga. 304 SS and fully insulated, wtih electronic condensate overflow protection. Mechanical float switches will not be accepted.
Fan motors shall be ECM type.
Filters shall be 1", MERV 4 rated.
Units shall include a non-fused disconnect switch, factory mounted and wired.
Unit shall include a solid-state control board as part of the unit control system incorporating these features: a. Random start compressor protection. b. Anti-short cycle compressor with 5-minute minimum OFF time delay. c. Safety controls that protect the compressor from the following conditions: i. High pressure ii. Low pressure iii. Low airflow iv. Low liquid flow v. Low entering air temperature vi. Brown-out power conditions vii. Low/High liquid temperature with user selectable settings based on liquid properties. d. Status LED indicating the device causing a fault condition shall be visible via a clear sight-glass such that access to unit interior is not needed to view status. e. Soft lockout feature that provides for an automatic reset prior to the initiation of a hard lockout. f. Test mode capability with shortened time delays for servicing. g. Condensate Overflow Protection - The unit will be supplied with solid-state electronic condensate over flow protection as standard. Mechanical float switches will not be accepted. h. Loss of Refrigerant Compressor Protection
Manuacturer to provide a 7-Day programmable thermostat with programmable fan mode.
3' Hose kits shall be braided stainless steel with Kevlar® reinforced core and fire rated. Optional ball valves, control valves, Y-strainers, etc., shall be provided as indicated in the control diagram(s).
Manufacturer to provide a 1 Year Parts and 5 Year Compressor Parts Warranty.
Whalen Advantage:
Smaller cabinet size
Quiet operation
Constant Torque ECM
Option for outside air-4" duct, ultra low constant fan
Comes in a 1/2 unit
Flexibility with knockouts
Option for single pipe unit
Leakage rating <5%