## Fan Coil
Fan Coil Competition Comparison
Item | Whalen | IEC | Rittling | Price | McQuay | JCI | Titus | Temspec
Exposed Cabinet Unit | No | Yes | No | No | No | Yes | No | Yes
Ditto (Back to Back) Unit | No | Yes | Yes | No | No | Yes | Yes | Yes
Master/Slave unit | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Removable Chassis | Yes | No | No | No | Yes | No | No | No
Supply/Return Riser Types | Type M or L | Type M or L | Type M or L | Type M or L | Type M, L, or K | Type M or L | Type M, L, or K | Type M or L
Drain Riser Type | Type M or L | Type M or L | Type M or L | Type M or L | Type PVC, M, L, or K | Type M | Type M, L, or K | Type M; uninsulated standard, insulated optional
Riser Extension | Type M or L | Type M or L | Type M or L | Type M or L |  | Type M or L | Type M, L, or K | Type M or L
Riser Diameter | 3/4" to 4" | 3/4" to 2-1/2" | 3/4" to 2-1/2" | 3/4" to 2-1/2" | 3/4" to 2-1/2" | 3/4" to 3" | 3/4" to 2-1/2"
Drain Riser Diameter | 3/4" to 1-1/2" | 1" to 1-1/4" | 3/4" to 1-1/2" | 3/4" to 1-1/4" | 3/4" to 1-1/4" | 3/4" to 1-1/4" | 3/4" to 1-1/4"
Riser Swaged End | Yes | Yes | Yes | Yes | No, Slip Couplings | Yes | Yes | Yes
Motor Type (Standard) | PSC - 115/208-230/277/1/60 | PSC - 115/1/60 | PSC - 115/1/60 | PSC - 115/208-230/277/1/60 | PSC - 115/1/60 | PSC - 115/1/60 | PSC - 115/1/60 | PSC - 115/1/60
Motor Type (Optional 1) | Hi-Static - 115/1/60 | PSC- 208-230/277/1/60 | PSC- 208-230/277/1/61 | ECM - 115/1/60 | PSC - 277/1/60 | PSC - 208-230/277/1/60 | PSC - 208-230/277/1/60 | PSC - 208-230/277/1/60
Motor Type (Optional 2) | ECM - 115/1/60 | Hi-Static - 115/208-230/277/1/60 | Hi-Static - 115/208-230/277/1/60 |  |  |  | ECM - 115/277/1/60 | ECM - 115/1/60
Motor Type (Optional 3) |  | ECM - 115/208-230/277/1/60 | ECM - 115/208-230/277/1/60
Motor Type (ECM) | Constant Torque Constant Air Volume Modulated Airlow | Constant Torque Constant Air Volume Modulated Airlow | Constant Torque Constant Air Volume Modulated Airlow | Constant Torque Constant Air Volume Modulated Airlow |  |  | Constant Torque Constant Air Volume Modulated Airlow
Coils (Standard) | 3-row (2-pipe) 3/1-row (4-pipe) both with manual air vent | 3-row (2-pipe) 3/1-row (4-pipe) both with manual air vent | 3-row (2-pipe) 3/1-row (4-pipe) both with manual air vent | 3-row (2-pipe) 3/1-row (4-pipe) both with manual air vent | 3-row (2-pipe) 3/1-row (4-pipe) both with manual air vent | 3-row (2-pipe) 3/1-row (4-pipe) both with manual air vent | 2-row (2-pipe) 2/1-row (4-pipe) both with manual air vent | 3-row (2-pipe) 3/1-row (4-pipe) both with manual air vent
Coils (Optional) | 4-row (2-pipe) 4/1-row (4-pipe) Automatic air vent | 4-row (2-pipe) 3/2-row or 4/1-row (4-pipe) Automatic air vent Union connections Stainless steel coil casings | 4-row (2-pipe) 3/2-row or 4/1-row (4-pipe) Automatic air vent Union connections | 4-row (2-pipe) 3/2-row or 4/1-row (4-pipe) Automatic air vent | 4-row (2-pipe) 4/1-row (4-pipe) automatic air vent Union connections | 4-row (2-pipe) 3/2-row or 4/1-row (4-pipe) Automatic air vent Stainless steel coil casing | 3-row (2-pipe) 4-row (2-pipe) 5-row (2-pipe) 3/1-row (4-pipe) 4/1-row (4-pipe) 2/2-row (4-pipe) 3/2-row (4-pipe) | 4-row (2-pipe) 3/2-row or 4/1-row (4-pipe) Automatic air vent
Drain Pan (Standard) | Stainless Steel w/ External Insulation Removable | Galzanized w/ Internal Insulation P-trap | Galzanized w/ Internal Insulation P-trap | Galzanized w/ Internal Insulation P-trap | Galzanized w/ Internal Insulation P-trap | Galzanized w/ Internal Insulation P-trap | Galzanized w/ Internal Insulation P-trap | Galzanized w/ Internal Insulation P-trap
Drain Pan (Optional) | None | Stainless Steel w/ External Insulation | Stainless Steel w/ External Insulation | Stainless Steel w/ External Insulation | Stainless Steel w/ External Insulation | Stainless Steel w/ External Insulation | Stainless Steel w/ External Insulation Removable | Stainless Steel w/ External Insulation Removable
Drain Pan Options | Condensate Pump Condensate Overflow Switch Vibration Isolator Pad | Condensate Overflow Switch | Condensate Pump, Condensate Overflow Switch | Condensate Overflow Switch | None | Condensate Overflow Switch | Double Wall Inner Wall Galvanized Inner Wall Stainless Condensate Overflow Switch | Condensate Overflow Switch Condensate Pump
Valve-Package (Standard) | 2-way Valve, 2 Ball Valves | None | 2-way or 3-way Valve, 2 Ball Valves | Isolation Ball Valves w/ Memory stop | None | 2-way or 3-way Valve, 2 Ball Valves, Motorized Valve | None | 2-way, 2 Ball Valves, Actuator
Valve-Package (Optional) | 3-way Valve Ball Valves Memory stop Modulating Valves Autoflow or Manualflow Valve P/T Taps Y-strainers Blow-off Valves Balancing Valves | 2-way Valve 3-way Valve Ball Valves Modulating Valves Autoflow or Manualflow Valve Circuit-Setter P/T Taps Y-strainers Blow-off Valves Balancing Valves | Ball Valves Modulating Valves Autoflow or Manualflow Valve Circuit-Setter P/T Taps Y-strainers Blow-off Valves Balancing Valves | 2-way Valve 3-way Valve Ball Valves Modulating Valves Autoflow or Manualflow Valve Circuit-Setter P/T Taps Y-strainers Blow-off Valves Balancing Valves | 2-way Valve 3-way Valve Ball Valves Modulating Valves Autoflow or Manualflow Valve Circuit-Setter P/T Taps Y-strainers Stainless Steel Braided Hoses Blow-off Valves Balancing Valves | Ball Valves Memory Stop Modulating Valves Autoflow or Manualflow Valve P/T Taps Y-strainers Stainless Steel Braided Hoses Actuators Balancing Valves Pressure/Temperature sensor Unions | 2-way Valve 3-way Valve Ball Valves Modulating Valves Autoflow or Manualflow Valve Memory Stop P/T Taps Y-strainers Actuators Balancing Valves Unions Stainless Steel Braided Hoses Blow-off Valves Pressure/Temperature sensor | 3-way Valve Ball Valves Modulating Valves Autoflow or Manualflow Valve P/T Taps Y-strainers Balancing Valves Floating point valve Actuator 0-10Vdc valve Actuator
Controls (Standard) | 115V T-stat Series 155 Surface mount Automatic changeover | None | Basic T-stat Manual speed control Surface mount Manual or Auto heat-cool changeover 115V | Basic T-stat Manual speed control Surface mount Manual or Auto heat-cool changeover Up to 277V | Basic T-stat 3 speed switch and Thermistor Surface mount Manual or Auto heat-cool changeover Up to 277V | None | None | Digital Display 3 speed fan switch Auto heat-cool changeover Unit mounted
Controls (Optional) | 24-volt or 115-volt T-stat 3 speed Fan Switch Digital or Digital Programmable T-stat Remote mount Unit mount DDC controls Transformer package Remote Control Relay | Various 24-volt or 115-volt T-stat 3 speed Fan Switch Digital or Digital Programmable T-stat Remote mount Unit mount DDC controls Transformer package | Various 24-volt or 115-volt T-stat 3 speed Fan Switch Digital or Digital Programmable T-stat Remote mount Unit mount DDC controls Transformer package | 24-volt 3 speed Fan Switch Digital Programmable T-stat Sequence-driven T-stat (ECM) Remote mount Unit mount DDC controls Transformer package | Various 24-volt or 115-volt T-stats Digital or Digital Programmable T-stat Remote mount Unit mount Quick Connect | Analog, digital display, or programmable t-stat Manual or Auto heat-cool changeover 3 speed Fan Switch Remote mount Unit mount or Wall mount DDC controls Fan-relay packages SCR fan-speed controller | Various 24-volt or 115-volt T-stats Manual or Auto heat-cool changeover Up to 277V 3 speed Fan Switch Remote mount Unit mount or Wall mount Analog and programmable t-stat Quick Connect | DDC Controls Face/Bypass Dampers in lieu of Valve Control Various 24-volt or 115-volt T-stats Manual or Auto heat-cool changeover Up to 277V Remote mount Wall mount
Electrical Options | Unfused or Fused disconnect switch 15, 20, 25, 30 amp Single point power connection | Unfused or Fused disconnect switch 20, 30, 40, 60 amp Single point power connection Motor Fusing | Unfused and Fused disconnect switch Single point power connection | Unfused and Fused disconnect switch Single point power connection Motor Fusing | None | Unfused and Fused disconnect switch Single point power connection Motor Fusing | Unfused and Fused disconnect switch Single point power connection | Unfused and Fused disconnect switch Single point power connection
Outdoor Air (Standard) | Outdoor Air (OA) opening Manual Controlled Damper | None | Outdoor Air (OA) opening Manual Controlled Damper | None | None | None | None | None
Outdoor Air (Optional) | Motorized Controlled Damper | Outdoor Air (OA) opening Manual Controlled Damper Motorized Controlled Damper | Motorized Controlled Damper | None | Outdoor Air (OA) opening Manual Controlled Damper Motorized Controlled Damper | Outdoor Air (OA) opening Manual Controlled Damper Motorized Controlled Damper | Outdoor Air (OA) opening Manual Controlled Damper Motorized Controlled Damper Freeze Protection | Outdoor Air (OA) opening Manual Controlled Damper Motorized Controlled Damper Intake Fan w/ Manual Speed Controller OA Chilled Water Coil
Cabinet Insulation (Standard) | 1/2" 2 pound density Thermal/Acoustical fiberglass | 1/2" Standard fiberglass | 1/2" 2 pound density Matt-faced fiberglass | 1/2" 1-1/2 pound density fiberglass | 1/2" Multi-densty fiberglass | 1/2" Thick Standard fiberglass | 1/2" Dual-densty fiberglass | 1/2" Standard fiberglass
Cabinet Insulation (Optional) | None | 1/2" Premium IAQ fiberglass 1/2" Foil Face 1/4" Closed Cell | 1/2" Foil Face 1/2" Closed Cell | 5/8" Foil Face 1/2" Fiber-free foam | 1/2" Closed Cell | Foil Face Closed Cell | 1" Dual-densty fiberglass 1/2" Foil Face 1" Foil Face | 1/2" Foil Faced 1/2" Closed Cell
Filters (Standard) | 1" MERV 4 Throwaway | 1" Throwaway non-woven synthetic | 1" Throwaway non-woven synthetic | 1" MERV 3 Throwaway | 1" Throwaway non-woven synthetic | 1" Throwaway non-woven synthetic | 1" Throwaway non-woven synthetic | 1" Throwaway non-woven synthetic
Filters (Optional) | 1" Permanent 1" MERV 8 Throwaway 1" MERV 13 Throwaway | 1" Permanent, 1" MERV 8 Pleated | 1" Permanent, 1" MERV 7 Pleated | 1" MERV 8 Pleated | None | 1" MERV 6 Pleated, Synthetic Media | 1" Pleated 1" Washable | 1" MERV 11 Pleated 1" Pleated
Supply Grilles (Standard) | Single Deflection aluminum | Double Deflection aluminum | Double Deflection aluminum | Single Deflection aluminum | None | None | None | Double Deflection steel, Powder coated Sight Baffle (If more than one Supply Opening)
Supply Grilles (Optional) | Single Deflection w/ White or custom paint Double Deflection Sight Baffle | Double Deflection w/ Opposed blade dampers Sight Baffle | Double Deflection w/ Opposed Blade Dampers Single Deflection | Double Deflection Double Deflection w/ Opposed Blade Dampers | Single Deflection Double Deflection Line-of-Sight Baffle | Double Deflection Double oulets Sight Baffle Opposed Blade Damper | Double Deflection Deluxe Aluminum Double Deflection Bar Type aluminum Opposed Blade Damper | Double Deflection Aluminum Opposed Blade Damper
Return Air Panel (Standard) | Stamped Louvered Grille | Stamped Louvered Grille | Stamped Louvered Grille Tamperproof screws Ivory paint | Stamped Louvered Grille White paint | Stamped Louvered Grille Ivory paint Plaster frame | Stamped Louvered Grille Powder Coated paint Quarter-turn cam-lock fasteners | Stamped Louvered Grille White Paint Powder Coated | Fixed Blade Grille White Enamel Hinged Filter Access door
Return Air Panel (Optional) | Removable Core aluminum Rear (p-trap) opening Tamperproof screws White or custom paint | Bar-Type aluminum finish Stamped Panel w/ Frame | Bar-Type aluminum finish Custom paint | None | Bar-Type aluminum finish w/ Ivory paint | Recessing Frame Full-face Aluminum | Invisislot Blank Front Panel with White Paint Deluxe Aluminum with Removable Core with White Paint Bar-Type aluminum with Removable Core Custom Paint Philips, Quarter, or Tamperproof fasteners | 1/4 Fasteners in lieu of Hinged Filter Acces Door Custom Paint
Openings | Factory Provided | Knockouts (Supply Grille, T-stat, Risers) | Knockouts (Supply Grille, T-stat, Risers) | Knockouts (Supply Grille, T-stat, Risers) | Factory Provided | Knockouts (Supply Grille, Risers) | Factory Provided | Knockouts (Risers, Thermostat) Factory Provided Supply Grille openings
Latest Update - 6-17-14
Notes:
All competitive data is aquired from catalog data and may not reflect what any of the companies are capable of providing as a non-cataloged special

## Heat Pump
Heat Pump Competition Comparison
Item | Whalen | ClimateMaster | JCI | Rittling | McQuay | Trane | Carrier
Water Source and Geothermal Heat Pump | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Water Source Heat Pump w/ Electric Heat (Boilerless Design) | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Water Source/Geothermal Heat Pump w/ Electric Heat (Supplemental) | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Water Source Air Conditioning Unit w/ Electric Heat | Yes | [5 empty] | Yes
Water Source Air Conditioning w/ Hydronic Heating | Yes | [5 empty] | Yes
Water Source Air Conditioning Unit | Yes | [5 empty] | Yes
Single Riser System | Yes | Yes | Yes | No | No | No | No
Removable Chassis | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Hose Kits | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Supply/Return Riser Types | Type M or L | Type M or L | Type M or L | Type M or L | Type M or L | Type M or L or K | Type M or L
Drain Riser Type | Type M or L | Type M or L | Type M or L | Type M | Type M or L or PVC | Type M or L | Type M or L
Riser Extension | Type M or L | Type M or L | Type M or L | Type M or L | Type M or L | Type M or L or K | Type M or L
Riser Diameter | 3/4" to 4" | 1" to 3" | 1" to 3" | 3/4" to 2-1/2" | 3/4" to 3" | 1" to 3" | 3/4" to 2-1/2"
Drain Riser Diameter | 3/4" to 1-1/2" | 3/4" to 1-1/2" | 3/4" to 1-1/2" | 3/4" to 1-1/4" | 3/4" to 1-1/2" | 1" to 3" | 1"
Riser Swaged End | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Motor Type (Standard) | PSC - 208-230/265/1/60 | PSC - 208-230/265/1/60 | PSC - 208-230/265/1/60 | PSC - 208-230/265/1/60 | PSC - 115/208-230/265/1/60 | PSC - 208-230/265/1/60 | PSC - 208-230/265/1/60
Motor Type (Optional 1) | Hi-Static - 208-230/265/1/60 | ECM - 208-230/1/60 | Hi-Static - 208-230/265/1/60 | Hi-Static - 208-230/265/1/60 | ECM - 115/208-230/265/1/60 | ECM - 208-230/265/1/60
Motor Type (Optional 2) | ECM - 208-230/265/1/60 |  | ECM - 208-230/265/1/60 | ECM - 208-230/265/1/61
Motor Type (Optional 3)
Motor Type (ECM) | Constant Torque Constant Air Volume | Constant Torque | Constant Torque | Constant Torque | Constant Torque | Constant Torque
Hot Water Coil (Standard) | 2-row |  |  |  | 3-row
Hot Water Coil (Optional) | 3-row in lieu of 2-row
Chassis (Optional) | Cupro-Nickel COAX coil | Cupro-Nickel COAX coil Non-plated Air to Refridgerant Heat Exchanger | Cupro-Nickel COAX coil Cupro-Nickel COAX coil - low temp option | Cupro-Nickel COAX coil | TXV Refrigerant Metering Device Cupro-Nickel COAX Coil | Cupro-Nickel COAX Coil | Cupro-Nickel COAX Coil
Drain Pan (Standard) | Stainless Steel w/ External Insulation Removable P-Trap | Galvanized Steel w/ Powder Coated Paint | Galvanized Steel | Stainless Steel Removable P-Trap | Corrosion Resistant ABS Plastic primary pan | Corrosion Resistant Material | Galvanized Steel secondary pan Removable P-trap
Drain Pan (Optional) | None | Stainless Steel | Stainless Steel | None | Stainless Steel secondary pan Galvanized Steel secondary pan | Galvanized Steel secondary pan | None
Drain Pan Options | Condensate Pump Condensate Overflow Switch Vibration Isolator Pad | Condensate Pump Condensate Overflow Switch Vibration Isolator Pad | Condensate Pump Condensate Overflow Switch Vibration Isolator Pad | Condensate Pump Condensate Overflow Switch Vibration Isolator Pad | Condensate Pump Condensate Overflow Switch Vibration Isolator Pad | Filter Maintenance Timer Condensate Overflow Switch | Condensate Overflow Switch Vibration Isolator Pad
Valve-Package (Standard) | None | None | None | None | None | None | None
Valve-Package (Optional) | 2-way Control Valves Ball Valves Water Regulating Valve Memory stop Autoflow or Manualflow Valve P/T Taps Y-strainers Petes Plug | 2-way Control Valves Ball Valves Water Regulating Valve Autoflow or Manualflow Valve P/T Taps Y-strainers | 2-way Control Valves 3-way Control Valves Ball Valves Water Regulating Valve Autoflow or Manualflow Valve P/T Taps Y-strainers | 2-way Control Valves Ball Valves Water Regulating Valve Autoflow or Manualflow Valve P/T Taps Y-strainers | 2-way Control Valves Ball Valves Water Regulating Valve Autoflow Valve P/T Taps | 2-way Control Valves Ball Valves Water Regulating Valve Autoflow or Manualflow Valve Strainer | 2-way Control Valves Ball Valves Water Regulating Valve Autoflow or Manualflow Valve Strainer P/T Taps Memory Stop
Controls (Standard) | 24-volt Manual Changeover Wall T-stat Remote mount (dependent on unit size) Unit mount (dependent on unit size) | 24-volt Manual Changeover Wall T-stat Series 155 T-stat Remote mount (dependent on unit size) Unit mount (dependent on unit size) | Microprocessor (MP) Control w/ 2-Speed Unit Mounted Switch | Microprocessor (MP) Control w/ 2-Speed Remote Mounted T-stat | None | Microprocessor (MP) Control Wall mount T-stat | Microprocessor (MP) Control Wall mount T-stat
Controls (Optional) | Digital Programmable Digital Non-programmable Manual Changeover Auto Changeover Random Start Relay Remote Control Relay Night Override Timer DDC/Solid State Controls T-stat Extension w/ plug out front of unit Special T-stat 2-speed Fan switch | Digital Programmable Digital Non-programmable Manual Changeover Auto Changeover Random Start Relay Remote Control Relay Night Override Timer w/ Pump Restart DDC/Solid State Controls T-stat Whip Communicating T-stat Single Stage, Multistage 2-speed Fan switch | Digital Programmable Digital Non-Programmable Manual Changeover Auto Changeover 7-day T-stat MP Ctrl w/ 2-Spd Thermostat MP Ctrl w/ 3-Spd Ctrl (ECM only) MP Ctrl w/ Surface-Mount Conn w/ Mounted Switch MP Ctrl w/ Surface-Mount T-Stat Conn w/ 2-Spd Ctrl MP Ctrl w/ Surface-Mount T-stat Conn w/ 3-SpdControl | Digital Non-programmable Digital Programmable T-stat Digitally Communicating T-stat Random Start Relay Remote Control Operation Quick Connect Unit Mount Wall Mount BAS | BACnet, LONworks Digital Non-programmable Digital Programmable T-stat 7-day T-stat Random Start Relay Remote Control Operation, Wireless Quick Connect Unit Mount Wall Mount Solid State Board BAS | BACnet DDC/Solid State Random Start Relay Remote Control Relay Digital Non-programmable Digital Programmable 7-day T-stat Communicating Module Zone Sensor Unit Mount | BACnet, LONworks Digital Non-programmable Digital Programmable T-stat 7-day T-stat Random Start Relay Remote Control Operation Quick Connect Unit Mount Zone Sensor
Electrical Options | Unfused or Fused disconnect switch 15, 20, 25, 30 amp Single point power connection Circuit Breaker | Unfused or Fused disconnect switch Single point power connection Circuit Breaker | Unfused or Fused disconnect switch Single point power connection Circuit Breaker | Unfused or Fused disconnect switch 20, 30 amp Single point power connection Circuit Breaker | Unfused or Fused disconnect switch Single point power connection Circuit Breaker | Unfused or Fused disconnect switch Single point power connection | Unfused or Fused disconnect switch Single point power connection
Outdoor Air (Standard) | None | None | None | None | None | None | None
Outdoor Air (Optional) | Outdoor Air Opening (OA) Internal Duct Plenum Kit Deep Cabinet (Special) Manual or Motorized Outdoor Air Damper | Outdoor Air Opening (OA) Plenum Manual or Motorized Outdoor Air Damper | Outdoor Air Opening (OA) Manual or Motorized Outdoor Air Damper | Outdoor Air Opening (OA) Manual or Motorized Outdoor Air Damper | None | None | Outdoor Air Opening (OA)
Cabinet Height Options | Shorter Units Stands 9" to 14" (Standard 6") Unit Stands 2" to 9" (Standard 6") Taller - Top Ducted Only | 80 " or 88" | 80" or 88" 4" or 8" stand | 88" | 80" to 96" | 80" or 88" | 80" or 88"
Cabinet Insulation (Standard) | 1/2" thick 2 pound density Thermal/Acoustical fiberglass | 1/2" thick 1-1/2 pound density Thermal/Acoustical fiberglass | 1/2" thick 2 pound density Thermal/Acoustical fiberglass | 1/2" thick 2 pound density Matt-faced fiberglass | 1/2" thick 1-1/2 pound density coated fiberglass | 1" thick closed cell insulation | 1/2" thick 1-1/2 pound density acoustic type fiberglass insulation
Cabinet Insulation (Optional) | 1" thick 1-1/2-pound density Thermal/Acoustical fiberglass insulated discharge plenum Elastomeric Closed Cell | None | None | 1/2" thick foil faced fiberglass with scrim and taped edges 1/2" thick elastomeric closed cell foam insulation | Closed-cell non-fibrous insulation | None | None
Filters (Standard) | 1" MERV 4 Throwaway | 1" MERV 8 Throwaway | 1" Throwaway | Washable Nylon | 1" Thowaway | 1" Throwaway | 1" cleanable aluminum mesh
Filters (Optional) | 1" Permanent Aluminum MERV 4 1" MERV 8 Throwaway 1" MERV 13 Throwaway | 1" MERV 11 Throwaway 2" MERV 8 Throwaway 2" MERV 11 Throwaway 2" MERV 13 Throwaway | None | 1" MERV 4 Throwaway | 2" Pleated | None | 2" Filter Rack
Supply Grilles (Standard) | Single Deflection aluminum Sight Baffle (When serving two or more rooms) | Single Deflection aluminum Sight Baffle (When serving two or more rooms) | Double Deflection w/ White paint Sight Baffle (When serving two or more rooms) | Single Deflection Sight Baffle (When serving two or more rooms) | Double Deflection w/ Adjustable blades | None | Double Deflection
Supply Grilles (Optional) | Single Deflection w/ White or custom paint Double Deflection Double Deflection w/ White or custom paint Opposed Blade Damper Special Grille Size or Special Location Tamperproof Screws | Double Deflection Opposed Blade Damper | Single Deflection Single Deflection w/ White paint Double Deflection Opposed Blade Damper | Single Deflection w/ White or custom paint Double Deflection Double Deflection w/ White or custom paint Opposed Blade Damper | Double Deflection w/ Extension Opposed Blade Damper | Single Deflection Single Deflection w/ White paint Double Deflection Double Deflection w/ White paint | Single Deflection Double Deflection w/ Opposed Blade Dampers
Return Air Panel (Standard) | Unit Mounted Acoustical Panel | Painted Flush Mounted Acoustical Panel | Painted Flush Mounted Acoustical Panel | Standard perimeter bypass Allen lock, Removable | Powder-coated White, Hinged | Painted Flush Mounted Acoustical Panel | Painted, Louvered Panel Tamperproof quarter-turn fasteners
Return Air Panel (Optional) | Flush Mounted Acoustical Panel Painted Flush Mounted Acoustical Panel Removable Core Air Return Grille Covered Air Opening Special Grile Size or Special Location Tamperproof Screws | Flush Mounted Acoustical Panel Tamperproof Screws | Flush Mounted Acoustical Panel | Perimeter bypass Allen lock or Key lock, Hinged Louvered Allen lock, Removable 6 Standard paint colors Custom paint | Removable | Flush Mounted Acoustical Panel | Bar-type aluminum Additional Colors Removable perimeter bypass Hinged perimeter bypass Keylock hinged perimeter bypass Removable louvered
Openings | Factory Provided | Knockouts in the field | Knockouts in the field | Knockouts in the field | Knockouts in the field | Knockouts in the field | Knockouts in the field
Ground Source Packages | Extended Range-Solid State Board-Water >50°F Geothermal-Solid state brd & low temp sensor >10°F Geothermal-Solid state brd & low temp sensor >20°F Geothermal-Solid state brd & low temp sensor >50°F | None | None | None | None | None | None
Sound Packages | "Anti Vibe" used inside Compressor Box Whisperline Silver - Rail Upgrade | "Ultra Quiet" package used inside Compressor Box | Compressor Box standard with insulation | None | None | Enhanced Reduction - used inside compressor box Deluxe Reduction - used inside compressor box, vibration pad between cabinet and chassis, extra dampening treatment | None
Latest Update - 7-25-14
Notes:
All competitive data is aquired from catalog data and may not reflect what any of the companies are capable of providing as a non-cataloged special